METRO EMERGENCY OPERATIONS CENTER OF KANAWHA COUNTY

501 Virginia Street, East

Charleston, WV  25301

### Request for Quotations

Re:	Transmitter Combiner, Receiver Multi-Coupler, Antennas, Feedline,  Any and All Related Hardware, and Installation for the Metro Emergency Operations Center of Kanawha County (Metro 911)

Date:	April 7, 2005

Bid Opening:	Bids must be received on or before Thursday, April 21, 2005, at 2:00 p.m., at the Metro Emergency Operations Center of Kanawha County, Charleston City Hall, 501 Virginia Street, East, Charleston, West Virginia 25301.

INSTRUCTIONS TO BIDDERS:

*PLEASE USE THIS FORM AS THE COVER SHEET FOR YOUR BID

1.	Bids must be received in a sealed envelope with the date and time of the bid opening on the outside of the envelope.  Faxed bids will not be accepted.

2.	Bid must be F.O.B. Delivery Point, unless otherwise indicated in proposal.

3.	All bids should be signed and in ink, showing all facts and the total amount of the bid.

4.	The Metro Emergency Operations Center of Kanawha County reserves the right to accept or reject in part or in whole any bid submitted, whichever is in the best interest of the Metro Emergency Operations Center of Kanawha County.

| Item No. | Description | Amount |
| --- | --- | --- |
| 1 | Transmitter Combiner, Receiver Multi-Coupler,Antennas, Feedline, Any and All Related Hardware, and Installation for the Metro Emergency Operations Center of Kanawha County per the Attached Specifications | $___________________ |

Vendor:  ___________________________    Signature:  __________________

Address:  __________________________     Date:  ______________________

__________________________________      Telephone:  _________________

METRO EMERGENCY OPERATIONS CENTER OF KANAWHA COUNTY

### Request for Quotations

ITEM:	Transmitter Combiner, Receiver Multi-Coupler, Antennas, Feedline,  Any and All Related Hardware, and Installation for the Metro Emergency Operations Center of Kanawha County (Metro 911)

LOCATION:	The Metro Emergency Operations Center of

Kanawha County

501 Virginia Street, East

Charleston, WV  25301

CONTACT:		Matt Gravely

Project Manager

(304) 357-0775 or mgravely@metro911.org

BID OPENING:	Bids must be received in a sealed envelope, with the date and time of the bid opening on the outside of the envelope, on or before Thursday, April 21, 2005, at 2:00 p.m., in the Metro Emergency Operations Center of Kanawha County, 	501 Virginia Street, East, Charleston, WV  25301.  Faxed bids will not be accepted.

SPECIFICATIONS:	The following specifications are intended to describe Transmitter Combiner, Receiver Multi-Coupler, Antennas, Feedline,  any and All Related Hardware, and Installation and the details contained in these specifications are not designed to exclude any vendor from bidding, but are offered as a means of describing the needs of the Metro Emergency Operations Center of Kanawha County.  Where brand names may be used, the words “or equal” are assumed to follow.  All specifications are minimum requirements.

1.1	INTRODUCTION

        - In order to minimize the number of antennas required on the new tower at their new 9-1-1 Center to interact with current public safety radio system, Metro       9-1-1 wants to install a Transmitter Combiner and Receiver Multi-Coupler at the site.  As part of this bid, the bidder will propose the combiner, multi-coupler, antennas, feedline, installation of equipment, and any related hardware (i.e., connectors, clamps) needed to complete the job.  All work must be done according to accepted engineering standards for public safety communication systems.

      - TRANSMITTER COMBINER

        - Capacity					16 channels

        - Technical specifications:

          - Specific frequencies			see below

          - Isolation - tx to tx			65 dB min

          - Isolation - antenna to rx		50 dB min

          - Input power per channel		not greater than 75 watts RF

          - Output power - combined		600 watts RF

          - VSWR					1.3: 1 or better

      - RECEIVER MULTI-COUPLER

        - Technical specifications

          - Channel capability			16

          - Bandwidth				20 MHz

          - System Gain				5 dB

          - Noise Figure				4.5 dB (max)

          - 3rd Order Intercept			+34 dBm.

          - Power input				120 VAC.

      - ANTENNAS AND COAX

        - The transmit/receive antennas will be appropriate to provide the required coverage.

        - The antenna systems will be connected via 7/8" LDF Heliax or larger transmission cable to the transmitter combiner, and 0.5" LDF Heliax or larger transmission cable to the receiver multicoupler.  The transmission cable type shall correspond to that needed to produce the specified coverage.

      - ANTENNA SYSTEMS

        - The transmitter / receiver antenna system will utilize separate transmitter and receiver antennas and be configured to support the sixteen (16) transmitters and receivers initially installed.

        - The Proposer shall provide specification sheets on the antennas (which include weight and wind loading information), receiver multi-couplers, transmitter combiners, and any other equipment deemed necessary by the Vendor for a complete system.

        - Transmitter combiner, receiver multi-coupler, filtering and pre-selector networks appropriate and suitable to provide the required coverage and performance shall be provided.

        - All antenna systems will be installed with proper lightning protection in accordance with EIA standards.

        - Mounting locations (“crows nest frames”) are already part of the tower.  Receive antennas will be mounted on the top frame, transmit on the lower frame (approximately 185’ and 175’ respectively).  Cable run from the antenna locations to the equipment room should not be more than 250’.

      - SPECIFIC TRANSMIT FREQUENCIES

        - The following frequencies will be the transmit frequencies to be combined

| - 153.785 | - 154.875 |
| --- | --- |
| - 158.760 | - 153.800 |
| - 154.950 | - 158.910 |
| - 159.060 | - 153.950 |
| - 158.940 | - 159.180 |
| - 155.730 | - 159.015 |
| - 154.4375 | - 156.1800 |
| - 158.9550 | - 159.4050 |

      - SPECIFIC RECEIVER FREQUENCIES

        - The following frequencies will be the receive frequencies which will run through the receive multi-coupler

| - 151.025 | - 151.100 |
| --- | --- |
| - 151.3025 | - 154.040 |
| - 154.055 | - 154.370 |
| - 154.965 | - 155.010 |
| - 155.025 | - 155.070 |
| - 155.625 | - 155.865 |
| - 156.195 | - 158.225 |
| - 158.730 | - 158.790 |

      - GENERAL INSTALLATION REQUIREMENTS

        - Installation shall include a complete, tested, system to include placement of associated cabling, appropriate system layout and terminal connections. Contractor shall provide associated power supplies and any other hardware, adapters and or connections to deliver a complete operable system to the Owner at the time of acceptance.

        - All installations shall be performed by factory authorized or Vendor affiliated service shops. Other shops or installers may be used upon mutual agreement between the customer and Vendor. Qualified, adequately trained personnel familiar with this type of work shall perform all installations. Vendors shall provide the names of the service shops, a summary of their experience and a list of five (5) references (minimum) for each proposed shop.

        - Prior to the start of the system installation the Contractor shall participate in a mandatory project site survey with the Owner or Owner’s representative to confirm actual equipment location within each space. At that time the exact equipment locations will be determined and documented by the Contractor.

        - The installation Contractor shall coordinate with others, as appropriate, to confirm that any prep work, such as tower work, coring, bracing, conduit, electrical, etc  that affects the installation of the base station equipment is complete before final inspection.

      - WARRANTIES

        - Any goods or services furnished by the selected Proposer under the contract shall be covered by the most favorable warranties provided by the Contractor to any customer; the rights and remedies hereby provided are in addition to any and do not limit those otherwise available to Metro 9-1-1.  The selected Proposer agrees that if such warranties are in any respect breached, the selected Proposer will pay to Metro 9-1-1 the full contract price agreed to by Metro 9-1-1 to be paid for the supplies, materials, equipment or services furnished under the bid or proposal. The terms of all warranties shall be finalized during contract negotiations.

ANTENNA FEED LINES  FL-LC1 (180' Tower)	   Quantity – Provide Unit Pricing in Increments of 100  feet

1	The contractor shall supply 2 feed lines in accordance

with the specifications set forth below.  An adequate

amount of feed line shall be supplied to the sixty (60)

foot level of the tower to the furthest rear wall of

the ham radio room.

2	The feed lines from the antenna shall be a continuous

length to the equipment room grounding bus bar with no

splices into the PolyPhasers. The feed lines from the

PolyPhasers shall be a continuous length to the

furthest rear wall of the ham radio room.

3	All connectors exposed to weather shall be sealed with

heat (or cold) shrink, 3M Super 88 tape and 3M Scotch Coat

to prevent moisture contamination.

3.1	All three forms of weather proofing shall be used on

each connector.

4	Grounding straps as recommended by the manufacturer shall

be supplied and installed on the feed line at the end

next to the antenna, at the bend next to the base of the

tower, prior to entering the building (or equipment room

grouding point and the grounding point located in the ham

radio room.

4.1	Transmission lines shall be supplied with mounting

hardware in sufficient quantity to ensure transmission

line is secured at manufacturers recommended intervals.

5	Transmission line shall be supplied with appropriate

connectors as specified in this section.

5.1	The antenna side of the transmission lines

shall be supplied with two (2) N female type connectors.

5.2	The equipment room side of the transmission lines

shall be supplied with four (4) N male type connectors

(one on each side of the PolyPhaser).

5.3	The ham radio room side of the transmission lines

shall be supplied with two (2) N female type connectors.

5.4	All connectors shall be of a type to negate dissimilar metal

characteristics at all locations.

6	If required, the feed line entering the equipment room shall be

formed into a drip loop to prevent moisture from entering the

building. If a drip loop is used, it shall not exceed the feed

line's minimum bending radius.

7	The antenna feed line shall meet the following technical

specifications:

Outer Conductor Diameter	7/8 inch (or larger)

Outer Conductor Type	Copper

Inner Conductor Type	Copper Clad Aluminum

Impedance			50 ohms

Jacket			Polyethylene

Dielectric			Low density foam

8	Two (2) Lightning Protectors, Bulkhead mount, 50-700 MHz

also rated for EMP, VHF 200 Watts, UHF 100 Watts,

2 female N connectors such as PolyPhaser IS-NEMP-C1

shall be provided.

9	All feed lines will be marked with cable markers and tagged

with description labels.

ANTENNA FEED LINES  FL-LC2 (130' Tower)	Quantity – Provide Unit Pricing in Increments of 100 Feet

1	The contractor shall supply 4 feed lines in accordance

with the specifications set forth below.  An adequate

amount of feed line shall be supplied to the one hundred

thirty (130) foot level of the tower to the furthest

rear wall of the ham radio room.

2	The feed lines from the antennas shall be a continuous

length to the equipment room grounding bus bar with no

splices into the PolyPhasers. The feed lines from the

PolyPhasers shall be a continuous length to the

furthest rear wall of the ham radio room.

3	All connectors exposed to weather shall be sealed with

heat (or cold) shrink, 3M Super 88 tape and 3M Scotch Coat

to prevent moisture contamination.

3.1	All three forms shall be used on each connector.

4	Grounding straps as recommended by the manufacturer shall

be supplied and installed on the feed line at the end

next to the antenna, at the bend next to the base of the

tower, prior to entering the building (or equipment room

grounding point and the grounding point located in the ham

radio room.

4.1	Transmission line shall be supplied with mounting

hardware in sufficient quantity to ensure transmission

line is secured at manufacturers recommended intervals.

5	A hoisting grip shall be supplied so as to permit four

4 separate runs of transmission line to be installed.

6	The hardline and coaxal transmission cables shall be supplied with

appropriate connectors as specified in this section.

6.1	The antenna sides of each transmission line

shall be supplied with four (4) N female type connectors

(total of four connectors).

6.2	All transmission line connectors located in the equipment room

shall be supplied with eight (8) N male type connectors.

(one on each side of the PolyPhaser).

6.3	The ham radio room side of the transmission line

shall be supplied with one (1) N female type connector

on the 7/8" hardline and three (3) UHF PL-259 connectors.

(total of four connectors).

6.4	All connectors shall be of a type to negate dissimilar metal

characteristics at all locations.

7	If required, the feed line entering the equipment room shall be

formed into a drip loop to prevent moisture from entering the

building. If a drip loop is used, it shall not exceed the feed

line's minimum bending radius.

8	One antenna feed line shall meet the following technical

specifications:

Outer Conductor Diameter	7/8 inch (or larger) hardline

Outer Conductor Type	Copper

Inner Conductor Type	Copper Clad Aluminum

Impedance			50 ohms

Jacket			Polyethylene

Dielectric			Low density foam

Three antenna feed lines shall meet the following technical

specifications:

Outer Conductor Diameter	RG-8 Type .405" (such as LMR 400-DB)

Outer Conductor Type	90% Tinned Copper

100% Aluminum foil tape

Inner Conductor Type	#10 AWG Solid Copper / .108"

Impedance			50 ohms

Jacket			Polyethylene UV resistant

Dielectric			Low density foam PE

Dry nitrogen injected

Attenuation			Shall not exceed db/100 @

30MHZ=0.7, 150=1.5, 450=2.7, 1.8GHz=5.7

9	One (1) Lightning Protector, Bulkhead mount, 50-700 MHz

also rated for EMP, VHF 200 Watts, UHF 100 Watts,

2 female N connectors such as PolyPhaser IS-NEMP-C1

shall be provided. (7/8" hardline)

Four (4) Lightning Protectors, Bulkhead mount, 50-700 MHz

also rated for 1.5-400 MHz, 250-3000 Watts, loss <0.1dB,

2 female N connectors such as PolyPhaser IS-B50HN-C0

shall be provided. (LMR-400-DB)

10	All feed lines will be marked with cable markers and tagged

with description labels.

ANTENNA FEED LINES  FL-LC3 (40' Light Poles)	      Quantity – Provide Unit Pricing in Increments of 100 Feet

1	The contractor shall supply 2 feed lines in accordance

with the specifications set forth below.  An adequate

amount of feed line shall be supplied to the forty

(40) foot level of light pole to the furthest

rear wall of the ham radio room.

2	The feed lines from the antennas shall be a continuous

length to the equipment room grounding bus bar with no

splices into the PolyPhasers. The feed lines from the

PolyPhasers shall be a continuous length to the

furthest rear wall of the ham radio room.

3	All connectors and open cable exposed to weather shall be

sealed with heat (or cold) shrink, 3M Super 88 tape and

3M Scotch Coat to prevent moisture contamination.

3.1	All three forms shall be used on each connector.

4	Transmission line shall be supplied with mounting

hardware in sufficient quantity to ensure transmission

line is secured at manufacturers recommended intervals.

5	A hoisting grip shall be supplied so as to permit two

(2) separate runs of transmission line to be installed.

6	The coaxal transmission cables shall be supplied with

appropriate connectors as specified in this section.

6.1	The antenna sides of each transmission line

shall be open, with no connectors, spooled

At the base of the light pole with four PL-259

UHF connectors and 2 double female SO-239

connectors (for installation by other than

contractor).

6.2	All transmission line connectors located in the equipment room

shall be supplied with four (4) N male type connectors.

(one on each side of the PolyPhaser).

6.3	The ham radio room side of the transmission line

shall be supplied with two (2) PL-259 UHF connectors.

(total of two connectors).

6.4	All connectors shall be of a type to negate dissimilar metal

characteristics at all locations.

7	If required, the feed line entering the equipment room shall be

formed into a drip loop to prevent moisture from entering the

building. If a drip loop is used, it shall not exceed the feed

line's minimum bending radius.

8	One antenna feed line shall meet the following technical

specifications:

Length			100 feet

Outer Conductor Diameter	RG-11

Outer Conductor Type	Copper

Inner Conductor Type	Copper

Impedance			75 ohms

Velocity Factor		0.66 (66%)

Jacket			Polyethylene

Dielectric			Low density foam

Two antenna feed lines shall meet the following technical

specifications:

Length			See section 1 of FL-LC3 (40' Light Poles)

Outer Conductor Diameter	RG-8 Type .405" (such as LMR 400-DB)

Outer Conductor Type	90% Tinned Copper

100% Aluminum foil tape

Inner Conductor Type	#10 AWG Solid Copper / .108"

Impedance			50 ohms

Jacket			Polyethylene UV resistant

Dielectric			Low density foam PE

Dry nitrogen injected

Attenuation			Shall not exceed db/100 @

30MHZ=0.7, 150=1.5, 450=2.7, 1.8GHz=5.7

9	Two (2) Lightning Protectors, Bulkhead mount, 50-700 MHz

also rated for 1.5-400 MHz, 250-3000 Watts, loss <0.1dB,

2 female N connectors such as PolyPhaser IS-B50HN-C0

shall be provided. (LMR-400-DB)

10	All feed lines will be marked with cable markers and tagged

with description labels.

REQUIREMENTS:

1.	Bid Documents – The Contractor is required to submit two (2) hard copies and six (6) electronic (disk) copies of the bid.

2.	Permits - The Contractor is responsible for all required notification and permitting requirements.  Copies of all documents are to be forwarded to the Metro EOC of Kanawha County.

3.	Property Damage - The Contractor shall be responsible for all damages to persons or property that may occur as a result of the Contractor’s fault or negligence until the completion of the project and final acceptance by the Metro EOC of Kanawha County.  Contractor hereby indemnifies, holds and saves harmless the Metro EOC of Kanawha County, the Kanawha County Commission, the City of Charleston, the State of West Virginia and the Federal Government free from any and all claims for damages sustained by the Contractor during performance of this contract, and hereby indemnifies the Kanawha County Commission, the State of West Virginia and the Federal Government against any claims arising from such work.

- Citations - In the event the Metro EOC of Kanawha County should be cited for a violation of any applicable State, Federal or local law, rule or regulation as a result of the Contractor’s actions associated with the activities described herein, Contractor shall reimburse the Metro EOC of Kanawha County for all attorney’s fees associated with the defense of same and also reimburse the Metro EOC of Kanawha County for any fines, penalties and other costs paid as a result of Contractor’s actions.

- 5.   Prevailing Wage Rates - State of West Virginia Prevailing Wage Rates, as established by the most recent publication of those rates, are required to be paid, for all non-exempt work performed by the Contractor.  Current Prevailing Wage Rates are available at www.wvsos.com/csr (click on the services icon for the 2005 wage rates). All payroll records are to be submitted to the Metro Emergency Operations Center of Kanawha County.  Payment of overtime, workers compensation and any other required coverage are the exclusive responsibility of the Contractor as required by local, State and/or Federal Laws or Regulations.

6.	Compensation - The Contract price shall be payable and paid in full after the Contractor has completed all work required under this Contract and the Metro EOC of Kanawha County shall have issued its Certificate of Acceptance certifying that all work as required under this Contract has been fully and satisfactorily completed and is accepted by the Metro EOC of Kanawha County.

7.	Bid Bond – A 5% Bid Bond is to be submitted with bid documents.

8.	Performance and Payment Bonds - A one hundred percent (100%) Performance Bond and a one hundred percent (100%) Payment Bond are required to be submitted to the Commission by the successful bidder.

9.	Inspections - All work under this contract shall be subject to inspection surveillance, and testing by the Metro EOC of Kanawha County at all reasonable times, both within the Project Area herein described and elsewhere. All such inspection(s) shall be performed in a manner as will not unduly delay the work.   Contractor warrants that the services and work are to be rendered and completed in a manner acceptable to the Metro EOC of Kanawha County and within the stated time.

10.	Work Performance - At any time during the performance of the work described or contemplated herein, or within 90-days after the issuance of a Certificate of Acceptance by the Metro EOC of Kanawha County, the Metro EOC of Kanawha County may require the Contractor to remedy, by whatever means necessary, and at no additional cost to the Metro EOC of Kanawha County, any failure by the Contractor to comply with the Contractor’s obligations to the Metro EOC of Kanawha County and to those State, Federal and Local Regulatory agencies having jurisdiction over the activities associated with the Scope of Work defined herein or as may be amended and mutually agreed upon by both parties in the future.

11.	Disputes and Arbitration -  ARTICLE 7 - ARBITRATION

A.	If, at any time, a difference of opinion or dispute shall arise between the parties to

this agreement with respect to any right or obligation arising under this agreement, the question in dispute, if it cannot be settled between the parties themselves, may be referred to arbitrators consisting of three competent and disinterested persons, one of which persons shall be selected by the Owner, one by the Contractor, and the third by the two arbitrators thus chosen by the Owner and Contractor.  The party desiring that any matter be submitted to arbitration shall give written notice thereof to the other party, stating therein the specific point or points in dispute and naming the person selected by said party as an arbitrator, and it shall be the duty of the other party, within fifteen days after receiving such notice, to agree in writing to submit the dispute to arbitration and to name an arbitrator.  If the party upon whom such notice is served fails to respond thereto with such fifteen day period, then such failure shall be deemed a refusal by such party to agree to submit the dispute to arbitration and civil action may be filed in the Circuit Court of Kanawha County, West Virginia, for the purpose of resolving the dispute.  In the event such other party does agree in writing to submit to arbitration but fails to name an arbitrator, the party desiring arbitration may apply to the Judge of the Circuit Court of Kanawha County, West Virginia, to appoint such arbitrator.  Likewise, in the event of the failure of the arbitrators thus named to agree upon the third arbitrator within twenty days after notification of their appointment, then the third arbitrator may be named by such Judge upon application of either party hereto, and such Judge is empowered to name such arbitrator.  The arbitrators thus chosen shall give to the parties to any dispute written notice of time and place of hearing and at the time and place appointed shall proceed with the hearing, unless, for some good cause of which the arbitrators, or a majority of them, shall be the sole judge, it shall be postponed until some later date within a reasonable time.  The discussion of the board of arbitrators thus constituted, or a majority of the persons composing the same, shall be made in writing and a copy thereof delivered to each of the said parties. Payment of the expenses of such arbitration, including the fees of the arbitrators, shall be as directed by the board of arbitration, or a majority thereof.

B.	If the parties hereto expressly agree to submit any dispute to arbitration as herein

provided then, and in such event, the decision rendered by the arbitrators shall be binding upon the parties and shall be specifically enforceable.  If the parties do not agree, in writing, to submit such dispute to arbitration, the party requesting such arbitration may file a civil action in the Circuit Court of Kanawha County for the purpose of resolving such dispute; however, a request for arbitration shall not be a prerequisite to filing a civil action to settle any such dispute.

C.	Where the parties have submitted any question to arbitration as herein provided,

the award of arbitrators shall be final and conclusive upon said parties with reference to the question so submitted an any judgment may be entered upon it in accordance with the provisions of Article 10, Chapter 55 of the Code of West Virginia, 1931, as amended.

12.	Termination of Contract and Liquidated Damages -  If the Contractor refuses or fails to perform this work with such diligence as will insure its completion within the time specified, including extensions, if any are granted, then the Metro Emergency Operations Center of Kanawha County (Metro 911), by written notice to the Contractor, Metro Emergency Operations Center of Kanawha County (Metro 911) may terminate the Contractor’s right to proceed with the work and this contract shall be terminated for any and all future work. On such termination, the may take over the work and prosecute the same to completion, by contract or otherwise, and the Contractor shall be liable to the Metro Emergency Operations Center of Kanawha County (Metro 911) for any additional costs incurred by the Metro Emergency Operations Center of Kanawha County (Metro 911) in the completion of the work. In addition, the Contractor shall also be liable for liquidated damages for any delay in the completion of the work as is provided in the paragraph immediately following.

If the work is not completed within six (6) months from the date of the executed Contracted, including authorized extension(s) (if any), the Contractor shall pay to the Metro EOC of Kanawha County liquidated damages (it being impossible to determine the actual damages occasioned by the delay) for each calendar day of unauthorized delay in completion of the work the sum of five hundred dollars per day ($500.00 per day); and the Contractor shall be liable to the Metro EOC of Kanawha County thereof.

13.	Compliance with Laws - The Contractor shall complete such action as is required to become fully informed of all State and Federal laws and local ordinances and regulations in any manner affecting those engaged or employed in the work, or the materials used in the work, or in any way affecting the conduct of the work.  The Contractor shall, at all times, observe and comply with and shall cause all the Contractor’s agents and employees to observe and comply with, all such existing and future laws, ordinances, regulations orders and decrees.  The Contractor shall further protect and indemnify the Kanawha County Commission and its officers and agents, from any claim or liability arising from or based on the violation of any such law, ordinance, regulation, order or decree, whether by the Contractor or the Contractor’s employees.

14.	Standards of Quality and Codes - All work must conform to all rules and regulations of all governmental authorities and agencies having jurisdiction over the project, including, but not limited to:

1.  Federal Occupational Safety & Health Administration Regulations

(OSHA)

2.  WV Department of Environmental Protection

3.  WV Bureau of Public Health

4.  WV State Fire Marshall

5.  WV Department of Natural Resources

For the Owner’s Record, submit copies of permits, licenses, certifications, inspection reports, releases, notices, receipts for fee payments, correspondence and records established in conjunction with compliance with standards and regulations bearing upon performance of work.

The Copeland “Anti-Kickback” Act - 	The Copeland Anti-kickback Act makes it a crime for anyone to require any laborer or mechanic employed on a Federal or Federally Assisted project to Kickback any part of his or her wages.

The Contract Work Hours and Safety Standards Act -  Requires overtime pay for laborers and mechanics at a rate of one and one-half times the basic rate of pay for hours worked on covered contracts in excess of 40 hours in a workweek.  This Act also requires the assessment of liquidated damages at the rate of $10 per day for each day that each laborer and mechanic worked without payment of the required overtime compensation.  The Act has no job site limitations.

Equal Opportunity Requirements - Title V of the Civil Rights Act of 1964 provides that no person shall be excluded from participation, denied program benefits or subjected to discrimination on the basis of race, color, or national origin.

Section 3 of the HUD Act of 1968, as amended, provides that to the greatest extent feasible, opportunities for training and employment shall be given to lower-income residents of the project area and that contracts for work to be performed be awarded to business firms located in or owned in substantial part by persons residing in the project area.

Section 109 of the HUD Act of 1974, as amended, provides that no person shall be excluded from participation (including employment), denied program benefits or subjected to discrimination on the basis of race, color, national origin, or sex under any program or activity funded under Title I of the HUD Act of 1974, as amended.

Executive Order 11246, as amended, provides that no persons shall be discriminated against, on the basis of race, color, religion, sex, or national origin in any phase of employment.

Executive Order 11625 provides that grantees establish affirmative action programs for minority business enterprise utilization.  Contractors are required to utilize maximum efforts to realize goals set forth in such programs.

### 15.	Workers Compensation & Unemployment Premiums - Contractor shall provide worker’s compensation and unemployment coverage for all Contractors’ employees.  Written documentation that Contractor’s workers compensation and unemployment premiums are current is required to be submitted by the successful bidder prior to commencement of work.

- Liability Insurance - Contractor is to provide liability coverage for all vehicles and equipment of Contractor with total limits of one million dollars ($1,000,000) per occurrence.  Prior to commencement of the project, successful Contractor is to provide proof of a minimum one million dollar ($1,000,000) per occurrence, commercial general liability insurance policy with the Metro Emergency Operations Center of Kanawha County named as additional insured.

## DOCUMENTS TO BE SUBMITTED WITH CONTRACTOR’S BID

The following documents are to be submitted with Contractor’s Bid and are considered a part of the contract document:

1.	5% Bid Bond

- Current Contractors License

3.	Completed Vendor Registration and Disclosure Statement (provided one is not currently on file)

4.	Signed and dated bid document

DOCUMENTS TO BE SUBMITTED BY SUCCESSFUL BIDDER

The following documents are to be submitted by the successful bidder prior to commencement of work and are considered a part of the contract document:

1.	Proof of insurance coverage with the Metro Emergency Operations Center of Kanawha County named as additional insured as stated above.

2.	100% Performance Bond.

3.	100% Payment Bond.

4.	Certification that Workers Compensation and Unemployment Premiums are current

The Metro Emergency Operations Center of Kanawha County reserves

the right to accept or reject, in part or in whole, any bid submitted,

whichever is in the best interest of the Metro Emergency Operations

Center of Kanawha County.